SPECIFICATIONS

MODELS 1000, 1001, 2000, 2001

Saino Economical Fire Door System

PART 1 – GENERAL

1.01 Work Included – Provide horizontal sliding fire door systems where shown on drawings and as specified herein.

1.02 Related Work – Opening preparation, miscellaneous or structural metal work, access panels, finish or field painting, field electrical wiring, wire, conduit, fuses and disconnect switches are in the Scope of Work of other divisions or trades.

1.03 Fire Rating – Doors shall bear the 3 Hour, UL Label (and the Factory Mutual Label if required).  Models 2000 and 2001 shall bear the 3-Hour, 250(, 30 minute temperature rise UL Label.

PART 2 – PRODUCTS

2.01  Manufacturer – Sliding fire doors are to be Model 1000, 1001, 2000 or 2001 as manufactured by Chase Industries, Inc., Cincinnati, OH.

2.02 Door Construction – Doors shall be constructed with 20 gauge steel skins securely bonded to a resin impregnated Kraft honeycomb paper core and 18 gauge interior framing channels.  (Substitute calcium silicate block insulation in place of Kraft honeycomb paper for 2000 or 2001 series doors.)  The doors shall be encased in heavy gauge perimeter channels.  Doors with multiple panels shall have the panels attached together by an interior “H” column, with the joint between the panels covered by a surface applied splice plate.  Doors shall be disassembled in sections for shipment.

2.03  Finish – Doors shall be prime painted with a high quality gray rust resistant paint.

Hangars are prime painted, all other hardware is powder coated.

2.04  Hardware – UL labeled hardware shall be furnished with the door and shall consist of 12 ga. box track, ball bearing, adjustable track brackets, wall bolts, flush cups, adjustable binders and guide rollers.

Specifications

Models 1000, 1001, 2000, 2001

Page -2 -

2.05  Closing System – Doors shall be furnished with a weight type closing system with 18 ga. weight box (or UL labeled Reel type closing system).  Thru wall link hardware will be furnished.

2.05a  Alternate Closing System -  An electronic closing system is available.  Model

F1900-PLC High Speed Closing System is recommended.

2.06  Options

a.  Controlled Speed Closing – A controlled speed closing system is available to prevent the door from abrupt closings.  For use with BOCA codes on fire doors with public egress applications.

b.  Heavier gauge box track systems available for large doors.

c.  Vision Panels – Doors bearing the 3 hour label may be furnished with vision panels, provided the area of exposed glass does not exceed 100 sq. in. for each vision panel and the vision panels are glazed with UL listed ceramic glass.

Doors bearing the 1-1/2 or 3/4 hour label may be furnished with wired glass vision panels.

For 1-1/2 hour rated doors, the area of exposed glass shall not exceed 100 sq. in.

For 3/4 hour rated doors the area of exposed glass shall not exceed 1296 sq. in with neither width nor height exceeding 54”.

d.  Gasketing – Perimeter gasketing is available to reduce air or smoke infiltration.

e.  Trackhoods – may be furnished to conceal track and hardware system.

f.  Pass Doors – One 3’0” x 7’0” personnel pass door is available in each door (one pass door per leaf in center parting doors).  Specify 1010, 1011, 2010 or 2011.

g.  Locking – Mortised sliding door locks or hasp and staple are available.

h.  Galvanized door available upon request.

i.  Stainless Steel – door and limited hardware available upon request, please consult factory.

j.  For situations with limited clearance, please consult factory.