SPECIFICATIONS

MODELS 50000,  50001

Saino Premounted Fire Door System

PART 1 – GENERAL

1.01 Work Included – Provide horizontal sliding fire door systems where shown on drawings and as specified herein.

1.02 Related Work – Opening preparation, miscellaneous or structural metal work, access panels, finish or field painting, field electrical wiring, wire, conduit, fuses and disconnect switches are in the Scope of Work of other divisions or trades.

1.03 Fire Rating – Doors shall bear the 4 Hour, UL Label .

PART 2 – PRODUCTS

2.01  Manufacturer – Sliding fire doors are to be Model 50000, 50001 as manufactured by Chase Industries, Inc., Cincinnati, Ohio.

2.02 Door Construction – Doors shall be made in modular sized panels, each panel being fabricated using a framework of 12 ga. channels welded at the corners with cross members not more than 48” on center.  Face sheets shall be a minimum of 20 ga. steel and shall be welded to the framework around the perimeter.  Panels shall be insulated with fiberglass insulation filling the space between the cross members.  Perimeter gasketing shall be furnished as standard.  Panels shall be connected with an interior “H” column with a cover plate.  A heavy gauge perimeter channel shall enclose the door with no visible face screws.

2.03  Finish – Doors shall be prime painted with a high quality gray rust resistant paint.

2.04  Hardware – UL labeled hardware shall be furnished with the door and shall consist of 7 ga.  track, ball bearing 3-1/8” diameter wheels with adjustable upthrust rollers and 7 ga. track brackets.  The track and brackets shall mount on a pre-engineered header casing with two jamb casings furnished.  A closed end trackhood shall be furnished.  UL labeled gaskets  furnished on all sides of the door panel.  All hardware shall be prime painted.

Specifications

Models 50000, 50001

Page -2 -

2.05  Closing System – Doors shall be furnished with a weight type closing system with 18 ga. weight box (or UL labeled Reel type closing system).  Thru wall link hardware will be furnished.

2.05a  Alternate Closing System -  An electronic closing system is available.  Model F1900 High Speed Closing System is recommended.

2.06  Options

a.  Controlled Speed Closing – A controlled speed closing system is available to prevent the door from abrupt closings.  For use with BOCA codes on fire doors with public egress applications.

b.  10 ga. box track system available for large doors or motor operated doors.

c.  Vision Panels – Doors bearing the 3 hour or 4 hour label may be furnished with vision panels, provided the area of exposed glass does not exceed 100 sq. in. for each vision panel and the vision panels are glazed with UL listed ceramic glass.

Doors bearing the 1-1/2 or 3/4 hour label may be furnished with wired glass vision panels.

For 1-1/2 hour rated doors, the area of exposed glass shall not exceed 100 sq. in.

For 3/4 hour rated doors the area of exposed glass shall not exceed 1296 sq. in with neither width nor height exceeding 54”.

d.  Crush Plates – are available for use on hollow block walls where cells of blocks are not filled with grout.

e.  Trackhoods – may be furnished to conceal track and hardware system.

f.  Pass Doors – Two personnel pass doors are available in each door ( two pass doors per leaf in center parting doors if opening is large enough to allow use.  Maximum size of personnel pass door is  3’8” x 7’0”.  Specify 50010 or 50011.

g.  Locking – Mortised sliding door locks or hasp and staple are available.

h.  Galvanized – door available upon request.

i.  Stainless Steel – door and limited hardware available upon request, please consult factory.

j.  For situations with limited clearance, please consult factory.